## Slide 1: ET TUTORIAL
Single Phase Transformer - Voltage regulation & Efficiency

## Slide 2
Ans:
1. A single phase t/f has a pu impedance of 0.1 and a pu resistance of 0.01. Calculate the voltage regulation at (a) 0.8 pf lag and (b) 0.8 pf lead

## Slide 3
2. A 10kVA 400/200V single phase t/f with a percentage resistance of 3% and a reactance of 6% is supplying a current of 50A to a resistive load. What is the value of the load voltage?
Ans:

## Slide 4
Ans:
3.

## Slide 5
Ans:
4.

## Slide 6
5.

## Slide 7
Ans:
6. A 20kVA 2000/200V 50Hz t/f has its LV side loaded fully at 0.8 pf lag. What is the maximum efficiency at this power factor and at what pu load is it achieved?

## Slide 8
Ans: (a) Pi = 9.87 kW, Pcu = 16.45 kW
(b) η = 95.14%
7. A 500 kVA t/f has an efficiency of 95% at full load and also at 60% of full load, both at upf.
Separate out the losses of the transformer.
Determine the efficiency at 3/4th full load.

## Slide 9
Ans: Volt regn = 2.4%, η = 98.2%
IHV = 63.63A, pf = 0.79 lag
8. For the 150 kVA, 2400/240V t/f whose circuit parameters are given as R1 = 0.2Ω, R2 = 0.002 Ω, X1 = 0.45Ω, X2 = 0.0045 Ω, Ri = 10 k Ω, Xm = 1.6 k Ω (as seen from 2400-V side). Draw the equivalent circuit as seen from the HV side and therefore determine the voltage regulation. Determine the efficiency when the transformer is supplying full load at 0.8pf lag on the secondary side at rated voltage. Under these conditions calculate the HV side current and its pf.